Specialty Class Meter

Model MVR

Scope

This specification covers cold water meters in sizes 3/4” through 6”.   The intended use of this specialty meter is to simplify applications by using one type of meter where three different types of meters would normally be used.  The meter specified here must be highly accurate, light weight and have minimal maintenance.

All meters must conform to applicable AWWA C-701 Class I Standards and this specification.

Type

Meters shall be of the Vertical Rotor Turbine type.  All water must pass through a measuring element.   Multi-Jet and Single Jet meters are not Vertical Rotor Turbine Meters.

Size

The size of the meter shall be determined by the nominal size opening of the inlet and outlet.

Length

Meters 3/4” through 2” shall be offered in compact as well as standard laying lengths as determined by AWWA C-700 as listed below.

| Size | Compact | Standard |
| --- | --- | --- |
| 3/4” | 7” | 9” |
| 1” | 9” | 10 3/4” |
| 1 1/2” | 9” | 13” |
| 2” | 10” | 17” |

Meters 3” through 6” shall be no longer than those listed below.

| Size | Length |
| --- | --- |
| 3” | 12” |
| 4” | 14” |
| 6” | 18” |

Main Case

The main case shall be constructed of a copper alloy containing not less than 81% copper.  The main case shall contain both the measuring element and the integral strainer.  3/4” through 2” shall be bottom case entry and 3” through 6” shall be of the top case entry design.

The size, model, direction of flow shall be cast in raised characters on the case.  The serial number shall be imprinted on both the body and the lid.

All 1 1/2” through 6” meters with standard laying length shall be equipped with test ports.

External Bolts

All external bolts, nuts and washers shall be of a non-ferrous material.

Flanges

Flanged ends 1 1/2” and 2” meters shall be of the oval type, 3” through 6” shall be round.

Threaded Ends

Meters 3/4” and 1” in size shall be Male Iron Pipe.  Meters 1 1/2” and 2” shall be Internal Pipe Thread.

Pressure Test

Meters shall be guaranteed to operate successfully at a working pressure of 150 PSI without leakage or damage to any part.

Registration

The registration shall be accurately recorded through the normal operating flow limits at not less than 98% nor more than 102% of actual throughput.  Accuracy at the specified minimum flow rate shall be at least 95% at the flow specified by size in the table below.

Size

Normal Operating Flow Range

| 98% - 102% | Minimum Flow Limits 95% |
| --- | --- |
| 3/4” | 1.0 - 30 GPM | .50 GPM |
| 1” | 1.5 - 50 GPM | .75 GPM |
| 1 1/2” | 2.0 - 100 GPM | 1.50 GPM |
| 2” | 3.0 - 160 GPM | 2.00 GPM |
| 3” | 4.0 - 350 GPM | 2.50 GPM |
| 4” | 5.0 - 650 GPM | 3.50 GPM |
| 6” | 15 - 1300 GPM | 5.00 GPM |

Registers

Registers shall be magnetic driven, straight reading, and provide easy to read visual registration at the meter.  Registers shall be permanently hermetically roll scaled utilizing an “L” shaped gasket between the copper housing and the register lens.  Registers shall contain a low flow indicator and a center sweep hand.  The unit of measurement shall be in U.S. Gallons/Cubic Feet.

Measuring Chamber

The measuring chamber shall be a turbine assembly mounted in a vertical orientation.  All water must pass through the measuring element.

The turbine will utilize a “Retro-Thrust” feature to reduce wear over the life of the meter.  Low flows will cause the rotor to wear against a sapphire bearing mounted in the top case of meter.  High flows will cause the turbine to pull down in the flow way to wear against a sapphire bearing located in the bottom of the hub assembly.

The inlet hub assembly shall include integral straightening vanes to eliminate the need for straight pipe diameters in front of or behind the meter.

Strainers

All meters must be provided with integral strainers.

Meters 3/4” through 1 1/2” shall have polymer type strainers while meters 2” and larger shall have stainless steel strainers.

All strainers must have an effective straining area of at least two (2) times the nominal pipe size of the meter.

Weight

The weight of the meter shall not exceed the following amounts:

| Size | Compact (lbs) | Standard (lbs) |
| --- | --- | --- |
| 3/4 | 4 | 5 |
| 1 | 7 | 10 |
| 1 1/2 | 10 | 13 |
| 2 | 16 | 20 |
| 3 |
| 38 |
| 4 |
| 68 |
| 6 |
| 140 |

Installation

The meter shall be designed so that no straight pipe diameters of pipe are needed upstream or downstream to properly install the meter and maintain its performance.  Meters shall be able to be installed in yokes, meter setters, or between elbows and maintain accuracy and performance.  Meters may be installed vertically or horizontally.

Remote Read/Automatic Meter Reading Capabilities

All meters shall be compatible and upgradeable to Visual Remote Read LCD Devices, Non-Contact Scan Read Pads, Inbound and Radio Read Devices without removal from service.  All systems will be comprised of “Solid State” electronic components.