Sample Specification

Water Meters:  5/8” – 2” Ultrasonic Solid State Meters

Scope:

This Specification covers Solid State Meter (SSM) bronze body, cold-water, ultrasonic meters compatible with open architecture radio equipment in 5/8" – 2” sizes and the materials employed in their fabrication. These meters shall offer a lead free alternative that encourages conservation, recycling, water purity and green life styles.

AWWA Standards:

- All Meters shall meet or exceed the latest version of the American Water Works Association Standard C715 for Cold Water Meters – Electromagnetic and Ultrasonic Type, For Revenue Applications requirements for accuracy and pressure loss.

- All Meters shall meet or exceed the American Water Works Association Standard C707 for Encoder-Type Remote-Registration systems for Cold Water Meters when equipped with an open architecture radio MIU or similar device.

NSF-61 Standards:

- All Meters shall comply with the latest EPA law and NSF-61 requirements governing potable water meters.

State No Lead and Low Lead Initiatives Standards:

- All Meters shall comply with the latest state no lead initiatives due to their unique design, which incorporates suitable materials for all wetted surfaces in the meter.

Main Case:

- Main case shall be composed of low lead copper alloy.

- Main case shall incorporate copper male threads to prevent crossed or stripped threads during installation when utilizing existing bronze couplings on ¾” – 1” sizes.

- Main case shall incorporate 2 bolt flanges to facilitate easy installation when utilizing 2 bolt oval flange kits with gaskets on 1.5” and 2” sizes.

- ¾” through 1” meters shall be provided with gaskets.

- Meters shall be pressure tested to ensure against leakage to a maximum 200 psi operating pressure.

- Meter case must and processor must be of a single unit design that discourages tampering.

- The meter case must display a raised indication of compliance with NSF-61.

- All processor housing sections must be sealed with a visible tamper indicator.

- The meter serial number shall be stamped on the processor housing and lid of the meter.

- The direction of flow shall be stamped on the processor surround and lid of the meter.

- Meter main case lengths must comply with comparable standard laying lengths for positive displacement meters in the same configuration as the solid state meters.

Measuring Chamber:

- Measuring chamber shall contain no moving parts.

- There shall be no customer serviceable components inside the meter or processor.

- O-ring seals shall be used throughout the measuring chamber to provide a more robust design. The use of glues and adhesives is not permitted.

- Measuring chamber shall maintain accuracy over the life of the meter and not suffer degradation due to mechanical wear.

- Measuring chambers shall be made of a suitable engineered polymer as described in AWWA C-715.

- Method of measurement shall be ultrasonic time transit measurement. Electromagnetic measurement is not permitted.

- Reflectors shall be made of stainless steel.

- Transducers shall resist corrosion and ensure reliable signal levels.

- The design of the tube shall channel water across the reflectors providing a cleaning effect that contributes to better operation and long term meter accuracy, improving utility revenues.

Headloss:

- Meters shall not exceed 2 PSI pressure loss at 15 GPM operating capacity for the 5/8” and ¾” sizes and 1.5 psi for the 1” size at 25 GPM operating capacity. 1.5” and 2” pressure loss shall not exceed 3.5 psi at 70 GPM and 110 GPM respectively.

Accuracy:

- Meters shall be 100% factory tested for accuracy and have the factory test results provided with each meter.

- Meter accuracy shall be +/- 1.5% in the normal operating flow range and -5% to +1.5% in the low flow range.

- The meter shall be accurate +/- 1.5% in the normal flow range of the meter up to 85 degrees F water temperature.

- Meters shall comply with the AWWA C715 new meter accuracy requirements from minimum flow to maximum flow for a period of 10 years from the date of shipment and offer a pro-rated warranty for years 11 through 20. See warranty document for specifics.

Strainers:

- All ¾” – 1” meters shall be provided with strainer screens installed in the meter.

- Strainers shall be rigid, fit snugly, be easy to remove.

Electronic Display Register:

- The processor shall be powered by a single A cell lithium battery that is permanently sealed to eliminate moisture intrusion.

- The display shall provide for standard visual registration at the meter of 0.1 gallons or 0.01 cubic feet.

- The display shall provide a series of icons that indicate various meter states.

- The numerals on the number wheels of the register shall not be less then 1/4" in height and should be legible at a 45-degree angle.

- Processors shall incorporate a low flow indicator.

- Processors shall incorporate a direction of flow indicator.

- Processors shall offer the option of registration in 0.1 gallons or 0.01 cubic feet.

- The processor shall incorporate an IR sensor that permits additional fields to be viewed on the processor.

- The IR sensor shall permit the download of additional data with the use of an IR Reader and software installed on a computer and to place the meter in test mode for additional granularity.

- The processor shall be secured to the meter main case by a tamper resistant method protecting against unauthorized removal of the processor from the meter body.

- The processor and meter shall be a single unit to prevent the removal from the body of the meter.

- The processor shall provide a true absolute encoder output that provides direct electronic transfer of meter reading information to any number of AMR/AMI device options.

- The encoder register shall send data in ASCII format (American Standard code for Information Interchange) to the interrogation device.

- The encoder register shall transmit the complete 8 digit serial number and complete 8 digit meter reading.

- An 8-digit register identification number that has been factory set and never duplicated shall be sent to the reading device.

- For all installations, the processor shall be permanently factory sealed with an epoxy coating of all terminal connections.  Meter requiring field sealing of the wire connection will not be allowed.

- All wiring for radio MIU’s shall be installed and potted by the manufacturer.

- Acceptable wiring configurations shall include 5’ flying lead wire, 18” Nicor connectors, and 5’ Itron cable connects. No other options are permitted.

- In line waterproof connections are required during installation for pit set encoder registers with Radio MIU’s to facilitate installation and field investigations.